# Article 5 – Technical Debt in Live Data Centers Is Operational Risk

Why temporary fixes, deferred decisions, and workaround culture silently erode resilience

Bagus Dwi Permana | 02 Feb 2026

## Abstract

In live data centers, technical debt does not appear as broken equipment or failed SLAs.
It appears as temporary fixes that never get reversed, undocumented deviations,
and growing reliance on tribal knowledge to keep systems running.
This article reframes technical debt as an operational risk mechanism rather than a software metaphor.
By correlating real operational patterns with safety science, resilience engineering,
and asset management literature, it shows how unmanaged technical debt increases incident probability,
extends recovery time, and reduces organizational learning.

## Opening

Every data center accumulates technical debt.
The difference between resilient sites and fragile ones is not whether debt exists,
but whether it is visible, bounded, and actively serviced.

The most dangerous words in critical operations are:
“Temporary solution—will fix later.”

## 1. From software metaphor to physical reality

The term “technical debt” originated in software engineering,
describing the future cost of quick fixes made today.
In data centers, the metaphor becomes literal.
A temporary bypass, a non-standard configuration,
or an undocumented parameter change behaves exactly like debt:
it accrues interest over time.

Unlike software, however, physical technical debt interacts with
thermal limits, electrical tolerances, and human memory.
The consequences are therefore nonlinear and harder to reverse.

## 2. What technical debt looks like in live facilities

Operational technical debt rarely appears as a single major deviation.
It accumulates as small, reasonable decisions:

• Temporary bypasses left in place after incidents
• PM scopes adjusted without updating acceptance criteria
• Alarm thresholds modified but not rationalized
• Vendor workarounds undocumented in SOPs
• Redundancy assumptions drifting from as-built reality

Individually, each change feels low risk.
Collectively, they redefine system behavior.

## 3. Latent conditions and drift toward failure

James Reason describes accidents as the alignment of latent conditions.
Technical debt is a systematic way of creating latent conditions.

As debt accumulates:
• System margins shrink
• Operator mental models diverge from reality
• Recovery paths become less certain

Drift toward failure does not require incompetence.
It requires time, success, and lack of visibility.

## 4. Human factors: memory as an unreliable control

When systems rely on memory to compensate for undocumented deviations,
they are no longer engineered systems—they are social systems.

Hollnagel’s Safety-II emphasizes that normal work must succeed reliably.
Technical debt shifts the burden of success from design to people,
increasing cognitive load and error likelihood during stress.

## 5. Case pattern: how debt amplifies incidents

Across multiple incidents, the same amplification pattern appears:

1. Incident occurs in a non-standard configuration.
2. Documentation does not reflect actual state.
3. Engineers lose time reconstructing history.
4. Recovery actions are conservative or delayed.
5. MTTR extends beyond design expectations.

In post-incident reviews, the root cause is often labeled
as “complexity” or “unexpected interaction”.
Technical debt is the missing name.

## 6. Why redundancy does not cancel technical debt

Redundancy protects against component failure,
not against misunderstanding of system state.

A redundant system operating under undocumented constraints
can fail faster than a simpler, well-understood one.
Technical debt undermines the assumptions redundancy relies on.

## 7. Asset management perspective (ISO 55000)

ISO 55000 emphasizes assurance, governance, and lifecycle thinking.
Unmanaged technical debt violates all three:

• Assurance: cannot be provided without truthful system state
• Governance: decisions made without traceability
• Lifecycle: temporary changes become permanent without review

From an asset management view,
technical debt is unmanaged lifecycle risk.

## 8. Designing a technical debt control system

Resilient sites treat technical debt as a controlled backlog,
not as an embarrassment to hide.

Key elements:
• Explicit classification: temporary, tolerated, prohibited
• Time-bound approvals with expiry dates
• Centralized deviation register linked to assets
• Mandatory reversal or formal redesign paths
• Review cadence aligned with risk, not convenience

Debt must be visible to be payable.

## 9. Quantifying debt impact (leading indicators)

While debt itself is abstract, its effects are measurable:

• Increasing MTTR variance
• Rising number of “known unknowns” during incidents
• Growing dependency on specific individuals
• Repeated PM findings on the same assets
• Escalation delays due to uncertainty

These are leading indicators of debt saturation.

## 10. Closing: resilience is debt-aware by design

Technical debt is inevitable in live operations.
Ignoring it converts short-term stability into long-term fragility.

Resilient data centers do not eliminate debt.
They make it visible, bounded, and continuously repaid.

## References

Reason, J. (1997). Managing the risks of organizational accidents. Ashgate.

Hollnagel, E. (2014). Safety-I and Safety-II: The past and future of safety management. Ashgate.

ISO. (2014). ISO 55000: Asset management — Overview, principles and terminology.

Weick, K. E., & Sutcliffe, K. M. (2015). Managing the unexpected.

Leveson, N. (2011). Engineering a safer world: Systems thinking applied to safety.